## Hoja1
[5 empty] | PROJECT: |  | BIOMERCADOS SANTA CECILIA |  |  |  | DATE: | 2017-03-02
VALENCIA
[5 empty] | PROJECT ID: |  | OM15-2441 |  |  |  | REV. #: | 0
RACK A
Refrigerant: |  | R-404A |  | Power Voltage: |  |  | 480/60/3 |  | Controller Type: |  | DANFOSS AK-SM880 LON RS485
Oil Type: |  | POE |  | Control Voltage: |  |  | 208-230/60/1
(Include step-down transformer)
-35ºF SUCTION GROUP
Refrigerant: |  | R-404A,DX
Condensing Temperatue: |  |  | 113°F
Subcooled Liquid Temperature: |  |  | 65°F
ID | Load Description |  |  | Dimensions (ft) |  |  | Model | kBTU/h | Room Temp. (˚F) | Evap. Temp. (˚F) | TD (˚F) | Defrost Type | Stub Sizes |  | Remarks
|  |  |  | L | W | H
LOOP A | [7 empty] | 59 |  | -16 |  |  | Liq.: 7/8" Suct.: 2 5/8" | [6 empty] | TES5 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | EVR | V. Bola Suc. | V. Bola Liq. | Filtros | V. Bola | V. Sol | Filtros | In | Out
A1 | General Freezer |  |  | 28.2 | 19.7 | 9.8 | (1) MPL-290 | 28.9 | -4 | -16 | 12 | EL | [7 empty] | 1 |  | 1 | [5 empty] | 6 | 2 1/8" (1) | 5/8" (1) | C-305 (1) | 2 1/8" (2) | EVR 6 (2) | C-084S (10) | 2 | 3
A2 | Fish Freezer |  |  | 16.1 | 13.1 | 9.8 | (1) MPL-290 | 30.1 | -4 | -16 | 12 | EL | [7 empty] | 1 |  | 1 | [5 empty] | 6 | 2 1/8" (1) | 5/8" (1) | C-305 (1) | 1 1/8" (10) | EVR 3 (10) | C-305S (2) | 2 | 3
LOOP B | [7 empty] | 68.2 |  | -33 |  |  | Liq.: 7/8" Suct.: 2 5/8" | [18 empty] | 5/8" (2)
B1 | Frozen Food Reach-In |  |  | (1) Giant BT 4P H20 |  |  |  | 8 | N/A | -29 | N/A | EL | [15 empty] | 3 | 1 1/8" (1) | 1/2" (1) | C-084 (1) | 1/2" (10) |  |  | 2 | 3
B2 | Frozen Food Reach-In |  |  | (1) Giant BT 4P H20 |  |  |  | 8 | N/A | -29 | N/A | EL | [15 empty] | 3 | 1 1/8" (1) | 1/2" (1) | C-084 (1) |  |  |  | 2 | 3
B3 | 8' Frozen Food Reach-In |  |  | (1) Cayman H20, 1x250 |  |  |  | 6 | N/A | -31 | N/A | EL | [15 empty] | 3 | 1 1/8" (1) | 1/2" (1) | C-084 (1) |  |  |  | 2 | 3
B4 | 8' Frozen Food Reach-In |  |  | (1) Cayman H20, 1x250 |  |  |  | 6 | N/A | -31 | N/A | EL | [15 empty] | 3 | 1 1/8" (1) | 1/2" (1) | C-084 (1) |  |  |  | 2 | 3
B5 | 12' Frozen Food Reach-In |  |  | (1) Cayman H20, 1x375 |  |  |  | 9 | N/A | -31 | N/A | EL | [15 empty] | 3 | 1 1/8" (1) | 1/2" (1) | C-084 (1) |  |  |  | 2 | 3
B6 | 8' Frozen Food Reach-In |  |  | (1) Cayman H20, 1x250 |  |  |  | 6 | N/A | -31 | N/A | EL | [15 empty] | 3 | 1 1/8" (1) | 1/2" (1) | C-084 (1) |  |  |  | 2 | 3
B7 | 8' Frozen Food Reach-In |  |  | (1) Cayman H20, 1x250 |  |  |  | 6 | N/A | -31 | N/A | EL | [15 empty] | 3 | 1 1/8" (1) | 1/2" (1) | C-084 (1) |  |  |  | 2 | 3
B8 | 6' Frozen Island |  |  | (1) Whale 2000 BT MT |  |  |  | 5.1 | N/A | -33 | N/A | EL | [15 empty] | 3 | 1 1/8" (1) | 1/2" (1) | C-084 (1) |  |  |  | 2 | 3
B9 | 12' Frozen Island |  |  | (1) Whale 2000 BT 375 |  |  |  | 9 | N/A | -33 | N/A | EL | [15 empty] | 3 | 1 1/8" (1) | 1/2" (1) | C-084 (1) |  |  |  | 2 | 3
B10 | 6' Frozen Island |  |  | (1) Whale 2000 BT MT |  |  |  | 5.1 | N/A | -33 | N/A | EL | [15 empty] | 3 | 1 1/8" (1) | 1/2" (1) | C-084 (1) |  |  |  | 2 | 3
[20 empty] | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0
Summary Suction Group |  |  | -35°F | Total Load: |  | 127.2 | kBTU/h
|  |  |  | Reserve: |  | 15%
|  |  |  | Required Cap.: |  | 146.28 | kBTU/h
|  |  |  | Evap.Temp.: |  | -33 | °F
|  |  |  | Heat Rejection: |  | 216.24 | kBTU/h
+12F SUCTION GROUP
Refrigerant: |  | R-404A
Condensing Temperatue: |  |  | 113°F
ID | Load Description |  |  | Dimensions (ft) |  |  | Model | kBTU/h | Room Temp. (˚F) | Evap. Temp. (˚F) | TD (˚F) | Defrost Type | Stub Sizes |  | Remarks
|  |  |  | L | W | H
[8 empty] | 654.1614 |  | 14 |  |  | N/A
- | LT Liquid Subcooler |  |  | N/A | N/A | N/A | N/A | 55.5864 | N/A | 14 | N/A | N/A
| MT Glycol Chiller 1 |  |  | N/A | N/A | N/A | N/A | 299.2875 | N/A | 14 | N/A | N/A
- | MT Glycol Chiller 2 |  |  | N/A | N/A | N/A | N/A | 299.2875 | N/A | 14 | N/A | N/A
Summary Suction Group |  |  | 12°F | Total Load: |  | 654.1614 | kBTU/h
|  |  |  | Reserve: |  | 0%
|  |  |  | Required Cap.: |  | 654.1614 | kBTU/h
|  |  |  | Evap.Temp.: |  | 14 | °F
|  |  |  | Heat Rejection: |  | 968.1589 | kBTU/h
+113ºF CONDENSING GROUP
ID | Description |  |  | Model |  |  |  | THR | Amb. Temp. (˚F) | Cond. Temp. (˚F) | TD (˚F) | Capacity (MBH) |  |  | Remarks
Reserva
540 RPM, Low Sound Level
- | Rack A Condenser |  |  | (2) ACC154-12D6A1A32B |  |  |  | 1184.3989 | 95 | 113 | 18 | 1221.3504 |  |  |  |  | 3.1199
[5 empty] | PROJECT: |  | BIOMERCADOS SANTA CECILIA |  |  |  | DATE: | 2017-03-02
VALENCIA
[5 empty] | PROJECT ID: |  | OM15-2441 |  |  |  | REV. #: | 0
MT SECONDARY LOADS
Secondary Fluid: |  | Propylene Glycol 35% V/V
ID | Load Description |  |  | Dimensions / Model |  |  | Model | MBH | Room Temp. (˚F) | Supply (˚F) | Return (˚F) | TD (˚F) | Flow (GPM) | Defrost Type | Remarks
|  |  |  | W (ft) | L (ft) | H (ft) | [10 empty] | Density: | 65.2 | lb/ft3 | AMI-140 |  | TWA-Z
LOOP C | [7 empty] | 319.4 |  | 19 |  |  | 60.6228 |  | Stubs Size: 3" NPT |  | Specific Heat: | 0.875 | BTU/lbF | DN32 | DN25 | DN20 | DN15
C1 | Deli & Dairy Cooler |  |  | 21 | 16 | 9.8 | FLW-3405A | 21.9 | 39.2 | 19 | 31.8 | 12.8 | 3.739 | OC |  | 118.9009 | [5 empty] | 1 | [12 empty] | 1 | 1
C2 | Deli Preparation Room |  |  | 16 | 14.5 | 9.8 | EDW-2306C | 17 | 50 | 19 | 38.8 | 19.8 | 1.8763 | OC |  | 72.8013 | Reserve: | 18.958 | GPM |  |  |  | 1 | [11 empty] | 1 | 1
C3 | Corridor, Section 2 |  |  | 28.6 | 11 | 9.8 | EDW-2406C | 20.1 | 50 | 19 | 42.4 | 23.4 | 1.8772 | OC |  | 79.5921 | [6 empty] | 1 | [11 empty] | 1 | 1
C4 | Returns Cooler |  |  | 13.5 | 7.9 | 9.8 | FLW-3406A C/R | 12.7 | 32 | 19 | 28.6 | 9.6 | 2.8911 | EL |  | 82.6841 | [5 empty] | 1 | [12 empty] | 2 | 3
C5 | Fish Cooler |  |  | 14.5 | 14.1 | 9.8 | FLW-4405A C/R | 16.8 | 32 | 19 | 28.8 | 9.8 | 3.7463 | EL |  | 107.8945 | [5 empty] | 1 | [12 empty] | 2 | 3
C6 | Fish Preparation Room |  |  | 15.1 | 9.8 | 9.8 | EDW-1406C | 13.5 | 50 | 19 | 34.7 | 15.7 | 1.8791 | OC |  | 65.206 | [6 empty] | 1 | [11 empty] | 1 | 1
C7 | Dock Area |  |  | 34.5 | 15.5 | 9.8 | EDW-5306C | 38.6 | 50 | 19 | 38.5 | 19.5 | 4.3259 | OC |  | 166.5471 |  |  |  |  | 1 | [13 empty] | 1 | 1
C8 | Fish Sale Area |  |  | 14.5 | 5.9 | 9.8 | EDW-1306C | 10.9 | 50 | 19 | 32.1 | 13.1 | 1.8184 | OC |  | 58.3692 | [6 empty] | 1 | [11 empty] | 1 | 1
C9 | Deli Sale Area |  |  | 29.2 | 6.2 | 9.8 | EDW-2306C | 14.9 | 50 | 19 | 43.7 | 24.7 | 1.3183 | OC |  | 57.6095 | [6 empty] | 1 | [11 empty] | 1 | 1
C10 | 12' Fish Curved Glass |  |  | (1) Piazzolla 3M1 1x375 |  |  |  | 5 | N/A | 19 | 28 | 9 | 1.2141 | EL |  | 33.9945 | [6 empty] | 1 | [11 empty] | 2 | 3
C11 | 24' Deli Curved Glass |  |  | (2) Piazzolla 3M2 2x375 |  |  |  | 10 | N/A | 19 | 28 | 9 | 2.4282 | OC |  | 67.9891 | [6 empty] | 2 | [11 empty] | 1 | 1
C12 | 24' Dairy Multideck |  |  | (2) Lion Large H20 2V 3M2 2x375 |  |  |  | 34 | N/A | 19 | 28 | 9 | 8.2558 | OC |  | 231.1629 |  |  |  |  | 2 | [13 empty] | 1 | 1
C13 | 24' Dairy Multideck |  |  | (2) Lion Large H20 2V 3M2 2x375 |  |  |  | 34 | N/A | 19 | 28 | 9 | 8.2558 | OC |  | 231.1629 |  |  |  |  | 2 | [13 empty] | 1 | 1
C14 | 8' Deli Multideck |  |  | (1) Serval Large 2V 3M2 MT200 |  |  |  | 9 | N/A | 19 | 28 | 9 | 2.1854 | OC |  | 61.1902 | [5 empty] | 1 | [12 empty] | 1 | 1
C15 | 24' Deli Multideck |  |  | (2) Serval Large 2V 3M2 2x375 |  |  |  | 26 | N/A | 19 | 28 | 9 | 6.3133 | OC |  | 176.7716 | [5 empty] | 2 | [12 empty] | 1 | 1
C16 | 24' Deli Multideck |  |  | (2) Serval Large 2V 3M2 2x375 |  |  |  | 26 | N/A | 19 | 28 | 9 | 6.3133 | OC |  | 176.7716 | [5 empty] | 2 | [12 empty] | 1 | 1
C17 | 8' Deli Multideck |  |  | (1) Serval Large 2V 3M2 MT200 |  |  |  | 9 | N/A | 19 | 28 | 9 | 2.1854 | OC |  | 61.1902 | [5 empty] | 1 | [12 empty] | 1 | 1
LOOP D | [7 empty] | 201.1 |  | 19 |  |  | 38.234 |  |  | 0
D1 | Corridor, Section 1 |  |  | 32.8 | 9.8 | 9.8 | EDW-2406C | 20.7 | 50 | 19 | 38.6 | 19.6 | 2.308 | OC |  | 89.0893 | [5 empty] | 1 | [12 empty] | 1 | 1
D2 | Meat Preparation Room |  |  | 16.4 | 14.1 | 9.8 | EDW-2306C | 17.1 | 46.4 | 19 | 38.8 | 19.8 | 1.8874 | OC | Stubs Size: 3" NPT | 73.2296 | [6 empty] | 1 | [11 empty] | 1 | 1
D3 | Meat Cooler |  |  | 16.4 | 12.8 | 9.8 | FLW-4405A C/R | 17.1 | 32 | 19 | 28.8 | 9.8 | 3.8132 | EL |  | 109.8212 | [5 empty] | 1 | [12 empty] | 2 | 3
D4 | F & V Preparation Room |  |  | 16.4 | 11.5 | 9.8 | EDW-2306C | 15.1 | 50 | 19 | 43.7 | 24.7 | 1.336 | OC |  | 58.3828 | [6 empty] | 1 | [11 empty] | 1 | 1
D5 | F & V Cooler |  |  | 16.4 | 12.8 | 9.8 | FLW-2303A | 16.4 | 42.8 | 19 | 31.2 | 12.2 | 2.9377 | OC |  | 91.6563 | [5 empty] | 1 | [12 empty] | 1 | 1
D6 | 12' Meat Multideck |  |  | (1) Lion Large H20 2V 3M1 1x375 |  |  |  | 19 | N/A | 19 | 28 | 9 | 4.6135 | EL |  | 129.1793 |  |  |  |  | 1 | [13 empty] | 2 | 3
D7 | 16' F & V Multideck |  |  | (2) Lion 1V H20 3M2 2x250 |  |  |  | 22 | N/A | 19 | 28 | 9 | 5.342 | OC |  | 149.576 |  |  |  |  | 2 | [13 empty] | 1 | 1
D8 | 24' F & V Multideck |  |  | (2) Lion 1V H20 3M2 2x375 |  |  |  | 32 | N/A | 19 | 28 | 9 | 7.7702 | OC |  | 217.5651 |  |  |  |  | 2 | [13 empty] | 1 | 1
D9 | 8' F & V Multideck |  |  | (1) Lion 1V H20 3M2 1x250 |  |  |  | 11 | N/A | 19 | 28 | 9 | 2.671 | OC |  | 74.788 |  |  |  |  | 1 | [13 empty] | 1 | 1
D10 | 20' F & V Multideck |  |  | (2) Lion 1V H20 3M2 1x375+250 |  |  |  | 27 | N/A | 19 | 28 | 9 | 6.5561 | OC |  | 183.5706 |  |  |  |  | 2 | [13 empty] | 1 | 1
D11 | Boards Room |  |  | 14.8 | 11.5 | 9.8 | FLW-2305C | 24.4 | 77 | 19 | 59.8 | 40.8 | 1.3069 | OC |  | 78.1546 | [6 empty] | 1 | [11 empty] | 1 | 1
[20 empty] | 0 | 13 | 12 | 11 | [11 empty] | 57 | 74
Summary HT Secondary Loads |  |  |  | Total Load: |  | 598.575 | MBH | [28 empty] | M. Expansión | 11.5625
Subtotal de Carga: |  | 520.5 | kBTU/h | Supply Temp.: |  | 19 | F | [28 empty] | Sensores | 57
Reserva (15%): |  | 78.075 | kBTU/h | Returns Temp.: |  | 30.8592 | [29 empty] | Fuente de P. | 2
Calor de Bombas: |  | 22.9 | kBTU/h | Total Flow: |  | 117.8148 | GPM | [28 empty] | M. Com. | 2
Note on I57: CALOR A DISIPAR POR OFERTA COSTAN